| Complete the installation checklist on page 2 of this form. Then complete the rest of the form. | STARTUP DATE: |
| --- | --- |
| This form is required for coverage under the Seneca limited warranty and must be completely filled out at the time of initial startup. Only authorized Seneca technicians can complete this form. This form must be signed by authorized Seneca technician and owner (or owners representative) and must be returned within 60 days. Warranty will commence on the startup date indicated herein. Return completed form by fax to 613-225-4690 or email to warranty@senecapowergeneration.com. | MONTH | DAY | YEAR |

| Authorized Seneca Representative Performing Startup |  | Owner Name/Unit Location |
| --- | --- | --- |
| Company Name |  |  | Company Name |  |
| Address |  |  | Unit Address |  |
| City |  |  | City |  |
| Prov/State |  |  | Prov/State |  |
| PC/Zip |  |  | PC/Zip |  |
| Country |  |  | Country |  |
| Telephone |  |  | Telephone |  |
|  |  |  | Round Trip Mileage from Nearest Authorized Seneca Distributor: |  |
| Equipment Information |
|  | Make | Model | Spec# | Serial# |
| Generator 1 | Seneca |  |  |  |
| Engine 1 |  |  |  |  |
| Alternator 1 |  |  |  |  |
| Generator 2 | Seneca |  |  |  |
| Engine 2 |  |  |  |  |
| Alternator 2 |  |  |  |  |
| ATS 1 |  |  |  |  |
| ATS 2 |  |  |  |  |
| ATS 3 |  |  |  |  |
| ATS 4 |  |  |  |  |
| Application Information |
| Check One: | Check One: | Check One: |
| Industrial Residential/Commercial | Stationary Mobile | Prime Standby Rental |

| Seneca Representative (Print) |  | Owner’s Representative (Print) |
| --- | --- | --- |
| Seneca Representative Signature and Date |  | Owner’s Representative Signature and Date |
| Signature | Month | Day | Year |  |  | Month | Day | Year |

Generator Set/Transfer Switch Installation Checklist

This document has generic content and some items may not apply to some applications. Check only the items that apply to the specific

application. Read and understand all of the safety precautions found in the Operation and Installation Manuals. Make the following

installation checks before performing the Startup Checklist.

Note: Use this form as a general guide, along with any applicable codes or standards. Comply with all applicable codes and standards.

Improper installation voids the warranty.

| EQUIPMENT ROOM OR WEATHER HOUSING |  |
| --- | --- |
| Y | N/A | # | ITEM |  | Y | N/A | # | ITEM |
|  |  | 1 | Is the equipment installed in a fire-resistant room (made of non-combustible material) or in an outdoor weather housing? |  |  |  | 25 | Is there an exhaust line condensate trap with a drain installed? |
|  |  | 2 | Is there adequate clearance between the engine and floor for service maintenance? |  |  |  | 26 | Is the specified silencer installed and are the hanger and mounting hardware tightened? |
|  |  | 3 | Is there emergency lighting available at the equipment room or weather housing? |  |  |  | 27 | Is a heat-isolating thimble(s) installed at points where exhaust lines pass through combustible wall(s) or partition(s)? |
|  |  | 4 | Is there adequate heating for the equipment room or outdoor weather housing? |  |  |  | 28 | Is the exhaust line free of excessive bends and restrictions? Is the backpressure within specifications? |
|  |  | 5 | Is the equipment room clean with all materials not related to the emergency power supply system removed? |  |  |  | 29 | Is the exhaust line installed with a downward pitch toward the outside of the building? |
|  |  | 6 | Is the equipment room protected with a fire protection system? |  |  |  | 30 | Is the exhaust line protected from entry by rain, snow, and animals? |
| ENGINE AND MOUNTING |  |  |  | 31 | Does the exhaust system outlet location prevent entry of exhaust gases into buildings or structures? |
|  |  | 7 | Is the mounting surface(s) properly constructed and leveled? |  |  |  | 32 | Are individuals protected from exposure to high temperature exhaust parts and are hot parts safety decals present? |
|  |  | 8 | Is the mounting surface made from non-combustible material? |  | AC ELECTRICAL SYSTEM |
|  |  | 9 | Was the generator-to-engine alignment performed after attaching the skid to the mounting base? Generator sets with two-bearing generators require alignment. Lubrication |  |  |  | 33 | Does the nameplate voltage/frequency of the generator set and transfer switch match normal/utility source ratings? |
| LUBRICATION |  |  |  | 34 | Do the generator set load conductors have adequate ampacity and are they correctly connected to the circuit breakers and/or the emergency side of the transfer switch? |
|  |  | 10 | Is the engine crankcase filled with the specified oil? Cooling and Ventilation |  |  |  | 35 | Are the load conductors, engine starting cables, battery charger cables, and remote annunciator leads installed in separate conduits? |
| COOLING AND VENTILATION |  |  |  | 36 | Is the battery charger AC circuit connected to the corresponding voltage? |
|  |  | 11 | Is the cooling system filled with the manufacturer’s specified coolant/antifreeze and purged of air? |  | TRANSFER SWITCH, REMOTE CONTROL SYSTEM, ACCESSORIES |
|  |  | 12 | Is there adequate inlet and outlet air flow (electric louvers adjusted and ventilation fan motor(s) connected to the corresponding voltage)? |  |  |  | 37 | Is the transfer switch mechanism free of binding? NOTE: Disconnect all AC sources and operate the transfer switch manually. |
|  |  | 13 | Is the radiator duct properly sized and connected to the air vent or louver? |  |  |  | 38 | Are the transfer switch AC conductors correctly connected? Verify lead designations using the appropriate wiring diagrams. |
|  |  | 14 | Are flexible sections installed in the cooling water lines? |  |  |  | 39 | Is there a UPS system? If yes, is the UPS installation checklist filled out? |
| FUEL |  |  |  | 40 | Is all other wiring connected, as required? Batteries and DC Electrical System |
|  |  | 15 | Is there an adequate/dedicated fuel supply? |  | BATTERIES AND DC ELECTRICAL SYSTEM |
|  |  | 16 | Are the fuel filters installed? |  |  |  | 41 | Does the battery(ies) have the specified CCA rating and voltage? |
|  |  | 17 | Are the fuel tanks and piping installed in accordance with applicable codes and standards? |  |  |  | 42 | Is the battery(ies) filled with electrolyte and connected to the battery charger? |
|  |  | 18 | Is there adequate fuel transfer tank pump lift capacity and is the pump motor connected to the corresponding voltage? |  |  |  | 43 | Are the engine starting cables connected to the battery(ies)? |
|  |  | 19 | Is the fuel transfer tank pump connected to the emergency power source? |  |  |  | 44 | Do the engine starting cables have adequate length and gauge? |
|  |  | 20 | Are flexible fuel lines installed between the engine fuel inlet and fuel piping? |  |  |  | 45 | Is the battery(ies) installed with adequate air ventilation? |
|  |  | 21 | Is the specified gas pressure available at the fuel regulator inlet? |  | SPECIAL REQUIREMENTS |
|  |  | 22 | Does the gas solenoid valve function? |  |  |  | 46 | Is the earthquake protection adequate for the equipment and support systems? |
|  |  | 23 | Are the manually operated fuel and cooling water valves installed allowing manual operation or bypass of the solenoid valves? |  |  |  | 47 | Is the equipment protected from lightning damage? |
| EXHAUST |  |  |  |  |  |
|  |  | 24 | Is the exhaust line sized per guidelines and does it have flexible connector(s)? Is the flexible connector(s) straight? |  |  |  |  |  |

Generator Set/Transfer Switch Startup Checklist

This document has generic content and some items may not apply to some applications. Check only the items that apply to the specific application.

Read and understand all of the safety precautions found in the Operation and Installation Manuals. Complete the Installation Checklist before

performing the initial startup checks.

| Y | N/A | # | ITEM |  | Y | N/A | # | ITEM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 | Verify that the engine is filled with oil and the cooling system is filled with coolant/antifreeze. |  |  |  | 27 | Disconnect the power switching device and logic controller wire harness at the inline disconnect plug at the transfer switch. |
|  |  | 2 | Prime the fuel system. |  |  |  | 28 | Manually transfer the load to the emergency source. |
|  |  | 3 | Open all water and fuel valves. Temporarily remove the radiator cap to eliminate air in the cooling system. Replace radiator cap in step 21. |  |  |  | 29 | Close the normal source circuit breaker or replace fuses to the transfer switch. |
|  |  | 4 | Place the generator set master switch in the OFF/RESET position. Observe Not-in-Auto lamp and alarm, if equipped, on the controller. |  |  |  | 30 | Check the normal source voltage, frequency, and phase sequence on three-phase models. The normal source must match the load. |
|  |  | 5 | Press the lamp test, if equipped on controller. Do all the alarm lamps on the panel illuminate? |  |  |  | 31 | Open the normal source circuit breaker or remove fuses to the transfer switch. |
|  |  | 6 | Open the main line circuit breakers, open the safeguard breaker, and/or remove fuses connected to the generator set output leads. |  |  |  | 32 | Manually transfer the load to the normal source. |
|  |  | 7 | Turn down the speed control (electronic governor) or speed screw (mechanical governor).* |  |  |  | 33 | Close the generator set main line circuit breakers, close the safeguard breaker, and/or replace the fuses connected to the transfer switch. |
|  |  | 8 | Verify the presence of lube oil in the turbocharger, if equipped. See the engine and/or generator set operation manual. |  |  |  | 34 | Place the generator set master switch in the RUN position. |
|  |  | 9 | Place the generator set master switch in the RUN position. Allow the engine to start and run for several seconds. |  |  |  | 35 | Check the generator set voltage, frequency, and phase sequence on three-phase models. The generator set must match normal source and load. |
|  |  | 10 | Verify that the day tank, if equipped, is energized. |  |  |  | 36 | Place the generator set master switch in the OFF/RESET position. |
|  |  | 11 | Place the generator set master switch in the OFF/RESET position. Check for oil, coolant, and exhaust leaks. |  |  |  | 37 | Open the generator set main line circuit breakers, open the safeguard breaker, and/or remove the fuses connected to the transfer switch. |
|  |  | 12 | Turn on the water/oil heaters and fuel lift pumps. |  |  |  | 38 | Reconnect the power switching device and logic controller wire harness at the inline disconnect plug at the transfer switch. |
|  |  | 13 | Check the battery charger ammeter for battery charging indication. |  |  |  | 39 | Close the normal source circuit breaker or replace fuses to the transfer switch. Place the generator set master switch to the AUTO position. |
|  |  | 14 | Place the generator set master switch in the RUN position. Verify whether there is sufficient oil pressure. Check for oil, coolant, and exhaust leaks. |  |  |  | 40 | Close the generator set main line circuit breakers, close the safeguard breaker, and/or replace the fuses connected to the transfer switch. |
|  |  | 15 | Close the safeguard circuit breaker. Adjust the engine speed to 50/60 Hz if equipped with an electronic governor or to 52.8/63 Hz if equipped with a mechanical governor.* |  |  |  | 41 | Place the transfer switch in the TEST position (load test or open normal source circuit breaker). NOTE: Obtain permission from the building authority before proceeding. This procedure tests transfer switch operation and connects building load to generator set power. |
|  |  | 16 | If the speed is unstable, adjust according to the appropriate engine and/or governor manual.* |  |  |  | 42 | Readjust frequency to 50 or 60 Hz with total building loads.* |
|  |  | 17 | Adjust the AC output voltage to match the load voltage using the voltage adjusting control. See the generator set/controller operation manual. |  |  |  | 43 | Verify that the current phase is balanced for three phase systems. |
|  |  | 18 | Allow the engine to reach normal operating coolant temperature. |  |  |  | 44 | Release the transfer switch test switch or close the normal circuit breaker. The transfer switch should retransfer to the normal source after appropriate time delay(s). |
|  |  | 19 | Check the operating temperature on city water-cooled models and adjust the thermostatic valve as necessary. |  |  |  | 45 | Allow the generator set to run and shut down automatically after the appropriate cool down time delay(s). |
|  |  | 20 | Manually overspeed the engine to cause an engine shutdown (68-70 Hz on 60 Hz models and 58-60 Hz on 50 Hz models). Place the generator set master switch in the OFF/RESET position.* |  |  |  | 46 | Set the plant exerciser to the customer’s required exercise period, if equipped. |
|  |  | 21 | Check the coolant level, add coolant as necessary, and replace the radiator cap. Verify that all hose clamps are tight and secure. |  |  |  | 47 | Verify that all options on the transfer switch are adjusted and functional for the customer’s requirements. |
|  |  | 22 | Place the generator set master switch in the RUN position. |  |  |  | 48 | If possible, run the building loads on the generator set for several hours or perform the load bank test if required. |
|  |  | 23 | Verify the engine low oil pressure and high coolant temperature shutdowns.* |  |  |  | 49 | Verify that all the wire connections from the generator set to the transfer switch and optional accessories are tight and secure. |
|  |  | 24 | Check the overcrank shutdown.* |  |  |  | 50 | If there is a UPS system, fill out the UPS prestart checklist and UPS startup checklist. |
|  |  | 25 | Place the generator set master switch in the OFF/RESET position. |  |  |  | 51 | Verify that the customer has the appropriate engine/generator set and transfer switch literature. Instruct the customer in the operation and maintenance of the power system. |
|  |  | 26 | Open the normal source circuit breaker or remove fuses to the transfer switch. |  |  |  | 52 | Fill out the startup notification at this time and send to the Generator Warranty Dept. Include the warranty form if applicable. |

* Some models with electronic engine controls may limit or prohibit adjusting the engine speed or testing shutdowns.